Go to: OVERVIEW (SaveOurCounty)     DETAILS (listener)     PLANNING     SCHOOLS     ENVIRONMENT     EROSION     Report corrections & broken links to Webmaster     Get updates on local issues

STATE OF WEST VIRGINIA

DEPARTMENT OF ENVIRONMENTAL PROTECTION

DIVISION OF WATER AND WASTE MANAGEMENT

# FACT SHEET

- NAME AND ADDRESS OF APPLICANT

CHARLES TOWN CITY OF

PO BOX 359

CHARLES TOWN, WV 25414

- NAME AND ADDRESS OF FACILITY

CHARLES TOWN, CITY OF

842 S. GEORGE STREET

CHARLES TOWN, WV 25414

- STATE NPDES APPLICATION NO.:  WV0022349

- COUNTY:     Jefferson

RECEIVING STREAM:  Evitts Run of the Shenandoah River of the Potomac River

- PUBLIC NOTICE NO. S-92-04

COMMENT PERIOD:  10-7-04 to 11-06-04

- SIC CODE(s)                   4952

- DESCRIPTION OF APPLICANT’S FACILITY OR ACTIVITY

To modify an existing 1.2 mgd sequencing batch reactor system to 1.75 mgd sequencing batch reactor system. Which, will include an addition of two (2) 2,430 SCFM blowers, a new 568,000 gallon aerobic digester with two (2) 2,300 SCFM blowers, convert existing aerobic digesters to sludge holding tanks, and all necessary valves, piping, controls, and other appurtenances.

- DESCRIPTION OF DISCHARGES (as reported by applicant):

Effluent Characteristics For Outlet No. 001

|  | Quantity | Other Units |
| --- | --- | --- |

| Parameter | ML Code | Season | Monthly Avg | Max | Units | Min | Monthly Avg | Max | Units |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BOD5 | A | Year Round | 107.58 | 927.29 | Lbs/day |  | 12.50 | 20.65 | Mg/l |
| Ammonia Nitrogen | A | Year Round | 26.62 | 241.77 | Lbs/day |  | 3.09 | 28.2 | Mg/l |

- PROPOSED EFFLUENT LIMITATIONS AND MONITORING REQUIREMENTS

Refer to attached Section A and DMR pages for the Draft Modification.

- RATIONALE FOR PROPOSED EFFLUENT LIMITATIONS AND MONITORING REQUIREMENTS

The City of Charles Town has been requested to provide sewage service for a number of new customers in the region.  To accommodate this request, the City has requested that the mass discharge limits of the existing NPDES permit remain the same.  This results in a more restrictive concentration limit for both BOD5 and ammonia nitrogen.

The Division has started to analyze the impacts of nutrients upon water quality and whether there is a need to establish nutrient water quality standards. Therefore, the Division shall impose effluent sampling for Total Nitrogen and Total Phosphorus in order to assist in this analysis.

##### RATIONALE FOR OUTLET 001

BOD5 	– (41.14 mg/l) Maximum Daily (20.57 mg/l) Avg. Monthly (1/Week)

– (600 lb/day) Maximum Daily (300 lb/day) Avg. Monthly (1/Week)

Technology based.

Ammonia Nitrogen   –  (6.74 mg/l) Maximum Daily  (3.37 mg/l) Avg. Monthly (1/Week)

– (98 lb/day) Maximum Daily (49 lb/day) Avg. Monthly (1/Week)

Water quality based – aquatic.

Total Nitrogen  – Monitor  (mg/l) Maximum Daily  (1/Quarter)

The Division has started to analyze the impacts of nutrients upon water quality and whether there is a need to establish nutrient water quality standards. Therefore, the Division shall impose effluent sampling for Total Nitrogen in order to assist in this analysis.

Total Phosphorus  – Monitor  (mg/l) Maximum Daily  (1/Quarter)

The Division has started to analyze the impacts of nutrients upon water quality and whether there is a need to establish nutrient water quality standards. Therefore, the Division shall impose effluent sampling for Total Phosphorus in order to assist in this analysis.

- RATIONALE FOR VARIANCE DECISIONS

N/A

- DETAILED DESCRIPTION OF LOCATION OF DISCHARGES(s)

| Outlet Number | Latitude | Longitude | Receiving Stream |
| --- | --- | --- | --- |
| 001 | 39º 16’ 44” N | 77° 51’ 24” W | Evitts Run |

- ANTIDEGRADATION

The outlet identified in the Permit modification is an existing outlet.  There is a proposed increase in the volume of discharges from the existing outlet from 1.2 mgd to 1.75 mgd.  In the case of BOD5, the quantity of pollutants to be discharged from the existing outlet will remain the same as the concentration limits will be reduced.     In the case of ammonia nitrogen, both the quantity and concentration will be reduced as aquatic life limits will be imposed.  The receiving stream (Evitts Run) is designated for all water use categories as defined in 46 CSR 1, Section 6.   The permit writer believes that the terms and conditions proposed in this draft modification will maintain and protect said waters.

- OTHER REQUIREMENTS

RATIONALE FOR “OTHER REQUIREMENTS” (C’ Conditions)

C.11 - Change of address for DEP.

C.12 – The permittee has previously addressed this condition.

C.13 – Change in reporting requirement specification from 1.08 mgd to 1.575 mgd because of expansion.

C.14 – Change in reporting requirement specification from 60,000 gpd to 87,500 gpd because of expansion.

C.23 –  self-explanatory.

The State of West Virginia, Department of Environmental Protection, Division of Water and Waste Management, has made tentative decisions on the application for a State NPDES Permit listed on this Fact Sheet.  In order to provide public participation on the proposed issuance of the required permit, the following information is being supplied in accordance with 47 CSR, Series 10, Section 11.3.e.2 and 3, of the West Virginia Legislative Rules.

During the public comment period, any interested person may submit written comments on the draft permit modification and may request a public hearing,  if no public hearing has already been scheduled.  A request for a public hearing shall be made in writing and addressed to:

Director, Division of Water and Waste Management, DEP

601 - 57th Street
Charleston, WV 25304

Attention:  Anne Howell, Public Information Office

The request shall state the nature of the issues proposed to be raised in the hearing, and must be received within the comment period.  The Director shall hold a public hearing whenever he, or she, finds, on the basis of requests, a significant degree of public interest on issues relevant to the draft permit modification.  Any person may submit oral or written statements and data concerning the draft permit modification, however, reasonable limits may be set upon the time allowed for oral statements, and the submission of statements in writing may be required.  A tape recording or written transcript of the hearing shall be made available to the public, upon request.

If information received during the public comment period appears to raise substantial new questions, the Director may reopen the public comment period.

All applicable information concerning the permit application and the tentative decisions is on file and may be inspected, by appointment, or copies obtained, at a nominal cost, at the offices of the Division of Water and Waste Management, 601 – 57th Street, Charleston, West Virginia, 25304, Monday through Friday (except State holidays) between 8:00 a.m. and 4:00 p.m.

Requests for additional information should be directed to Anne Howell at (304) 558-4253.  Our TDD number is (304) 558-2751.